Basic Small Messages Protocol
(BSMP)

Version 2.10
  August 9th, 2014

Bruno Martins
bruno.martins@lnls.br
Controls Group
Revision History
Revision	Changes
2.10 / 08/09/2014	Add a new error code: (0xE8) Resource Busy.
2.00 / 02/12/2014	Change the name of the protocol. / Was: Sirius Low Level Protocol (SLLP).
2.00-rc2 / 01/24/2014	Add the possibility of a Curve block contain less than SBLOCK bytes of data.
2.00-rc1 / 01/23/2014	First release candidate.

# Introduction

In order to standardize all communications between equipment developed for the Sirius project and connected to the Controls Network, a common communication protocol was created. The protocol was named Basic Small Messages Protocol – BSMP. This protocol describes two layers: transport and application. Those layers are independent from one another.

The Sirius' Controls Network is composed of Ethernet and RS485 networks. The devices residing in the lowest levels of the hierarchy will communicate over RS485 with Single Board Computers (SBC). The SBC's, in turn, will communicate with the computers in the higher level of the hierarchy through Ethernet, therefore having a role of a gateway between Ethernet and RS485 networks.

All RS485 devices developed for the Sirius accelerator that will connect to the Controls Network must use both layers described in this document. All Ethernet devices must use UDP/IP or TCP/IP and the application layer described in this document in order to communicate with a SBC.

# Transport Layer

The transmission unit of the Transport Layer is the packet. Each packet holds a message. The Transport Layer requires all data in a packet to be in binary, which means that no byte value should have special meaning. The end of a packet is indicated with a silence on the Serial line with duration of 2 bytes. For example, in a 10 Mbps Serial network the silence after a packet should last 1.6 μs. This layer does not impose a size limit on the message inside a packet.

Addressing	Message					Checksum
DESTINATION					CHECKSUM

Table 1- Structure of a Transport Layer packet
Packets in the Serial network	have a well defined format. The first byte is used for addressing and should have a valid address of a device or group of devices. If the packet is from a node to a master, DESTINATION must be 0. The last byte of the packet must be the CHECKSUM. This structure is shown in the Table 1. The CHECKSUM is the sum of all Addressing and Message bytes, in 2's complement. Therefore, the sum of all bytes of a valid packet must be equal to zero (8-bit sum). Each packet carries only one message.

## Addressing
The devices in a serial network must be given an address between 0 and 31, inclusive. This range restricts the existence of only thirty two devices in a single serial network. The device with address 0 is the master of the network, the other devices being nodes (or slaves). Every network must have exactly one master and at least one node.
## Multicast groups
Nodes	can be part of Multicast Groups. A Multicast Group can have an address between 248 and 255, which allows the existence of up to eight of such groups. The Multicast Group with address 255 is a special Group called Broadcast. All devices in a serial network must be in the Broadcast Group. A node can belong to more than one Multicast Group. The address ranges of serial networks are specified in the Table 2.

Address range	0	1 to 31	32 to 247	248 to 254	255
Used for	Master	Node	Reserved	Multicast Group	Broadcast

Table 2- Addresses on the Serial network

# Application Layer

The Application Layer defines all the messages that can be exchanged between devices and the actions that must be taken in response to a message.
## Concepts

This section defines the concepts that will be used to describe the Application Layer.
### Network, Message, Command, Master and Node (or Slave)

Devices connected with BSMP are components of a network. Network components communicate exchanging messages. Each message holds a command, that can be either a request or a response.
Network components can perform one of two roles: master or node (also called slave). There must be exactly one master per network. The amount of nodes in a network is not limited by the Application Layer.
### Protocol Type

The protocol here described is a token protocol. Only the device with the token can initiate a transmission in the network. In this protocol the token is implicit. Therefore, all communications are initiated by the master. Once the master sends a direct message to a node, it is understood that the node has the token until it answers the master, returning the token. The protocol is stateless: each pair request/response is a whole independent transaction.
The protocol is byte oriented, which means that the smaller unit of the message is one byte. Multi-byte values are big endian.
If the Application Layer is used together with the Transport Layer, two restrictions apply:

1. Multicast packets must not be answered.
2. The master must establish a timeout to avoid the loss of the token.

### Message Structure

A protocol message must have at least three bytes, which are part of its header: COMMAND and LENGTH (with two bytes). The COMMAND field specifies which command should be executed by the node or the response of the execution of a command. All the commands of the protocol are described in the section Protocol Commands. The field LENGTH holds the length of the Payload of the message, in big endian. If the message has no payload, both LENGTH bytes must be 0. The structure of the message is depicted in Table 3. The field LENGTH can assume values between 0 and 65535.
Header			Payload
COMMAND	LENGTH	LENGTH

Table 3- Structure of a BSMP's message
## Entities

Devices communicate with each other in order to manipulate Entities of the protocol. Entities fall on one of four categories: Variable, Group of Variables, Curve and Function. The maximum amount of each entity in a node are listed in Table 4. Every Entity is identified by an ID. An ID must be unique within a category. IDs must start with 0 and be continuous within each category. For instance, the Variables of a node with 4 Variables must have the IDs 0, 1, 2 and 3. If the same node also has 8 Curves, their IDs must be 0, 1, 2, 3, 4, 5, 6 and 7.

Entity	Maximum Amount	Properties
Variable	128	ID, TYPE, SIZE
Group of Variables	8	ID, TYPE, SIZE
Curve	128	ID, TYPE, SIZE, CHECKSUM
Function	128	ID, INPUT, OUTPUT

Table 4- Amounts and properties of the protocol's Entities
### Variable

The Variable is the central Entity of the protocol. Each node has a number of Variables. Each Variable has a value that can be read from and, for writable Variables, written to. The meaning of each Variable must be specified by the device developer. Each Variable has one value and three properties, listed in Table 5. It's important to stress that a writable Variable can also be read (in which case the read value would be the last written value). However, to write in a read-only Variable must not be allowed.

Property	Description
ID	Unique number that identifies the Variable
TYPE	The Variable may be read-only (TYPE 0) or writable (TYPE 1)
SIZE	The length of the Variable's value, between 1 and 128

Table 5- Properties of a Variable

### Group of Variables

It is possible to create Groups of Variables so that some sets of Variables can be read from or written to with a single command. Each Group of Variables has three properties and a list of Variables in the Group, according to Table 6. A Variable can belong to more than one Group. There must exist, at all times, at least three Groups of Variables, presented in Table 7. Those Groups are called Standard Groups, which must not be deleted. A writable Group must contain only writable Variables. However a read-only Group may contain both writable and read-only Variables.

Property	Description
ID	Unique number that identifies the Group
TYPE	The Group may be read-only (TYPE 0) or writable (TYPE 1)
SIZE	The amount of Variables in the Group, between 1 and 128

Table 6- Properties of a Group of Variables

ID	TYPE	Group's Variables
0	0	All Variables of a node
1	0	All read-only Variables of a node
2	1	All writable Variables of a node

Table 7- Standard Groups of Variables

### Curve

A Curve is a long sequence of bytes, which may or may not be related to each other. Values of a Curve can be transmitted in either direction (master → node or node → masted). A Curve has five properties, listed in Table 8.

Property	Description
ID	Unique number that identifies the Curve
TYPE	The Curve may be read-only (TYPE 0) or writable (TYPE 1)
SBLOCK	The size of an individual block, between 1 and 65520
NBLOCKS	The amount of blocks in the Curve, between 1 and 65536
CHECKSUM	MD5 hash of all values of a Curve

Table 8- Properties of a Curve
The TYPE property indicates if the values of a Curve can (1) or cannot (0) be written to. The Curve's size is limited to 65536 (216 ) blocks, each block being, at most, 65520 bytes long, which gives a total of 4095 MiB per Curve. The NBLCOKS field is the number of blocks of a Curve. The SBLOCK field is the maximum size of a single block. A Curve may have a CHECKSUM associated with it, which must be calculated using the MD5 algorithm. Therefore, the length of the CHECKSUM field is 16 bytes.
### Function

A Function is a kind of a Remote Procedure Call – RPC. A Function can receive between zero and fifteen bytes as input and return between zero and fifteen bytes as successful output or one byte as error output. A successful return is signaled by the command (0x51) Function Return; an error in the execution of the Function is indicated by the command (0x53) Function Error. The meaning of the input bytes, the output bytes and the error codes is specific to each Function and must be provided by the developer of the device. The properties of a Function are described in Table 9.

Property	Description
ID	Unique number that identifies the Function
ENTRADA	Amount of bytes taken as input (between 0 and 15)
SAIDA	Amount of bytes returned as output (between 0 and 15)

Table 9- Properties of a Function

## Protocol Commands

All the codes accepted in the field COMMAND of the messages and their meaning and structure are described in this section. The commands are divided in classes, being grouped by their semantic likeness. Each command code is consisted of one byte, being the most significant nibble the indicative of the command's class. In general, the convention for the command's codes is that even codes are for commands from the master to the slave and odd commands from the slave to the master. The exceptions are the error codes (section (0xE_) Error Commands), which are always from the slave to the master, and the (0x41) Curve Block command, which can be sent both ways.
If a node happens to receive a message in which the number of bytes indicated in the LENGTH field differs from the actual length of the Payload, it will return the error (0xE1) Malformed Message. If a node receive a command that it doesn't know how to perform, it will return the error (0xE2) Operation not supported. If the number of bytes in the payload of a command differs from the number of bytes expected for that specific command, the error (0xE5) Invalid Payload Size will be returned.
 A summary of all commands of the protocol and their payloads is given in Table 10. Detailed descriptions are given in the following sections.
(Code) Command	Direction	Payload
(0x00) Query Protocol Version	M → N
(0x01) Protocol Version	M ← N	[Version, Subversion, Revision]
(0x02) Query List of Variables	M → N
(0x03) List of Variables	M ← N	[ Type | Size] * (# of Vars)
(0x04) Query List of Group of Variables	M → N
(0x05) List of Group of Variables	M ← N	[ Type | Size] * (# of Groups)
(0x06) Query Group of Variables	M → N	[Group ID]
(0x07) Group of Variables	M ← N	[Var ID] * (# of Vars in the Group)
(0x08) Query List of Curves	M → N
(0x09) List of Curves	M ← N	[Type,NBlocks(2 bytes),SBlock(2 bytes)]*(# curves)
(0x0A) Query Curve Checksum	M → N	[Curve ID]
(0x0B) Curve Checksum	M ← N	16 bytes (MD5 Checksum)
(0x0C) Query List of Functions	M → N
(0x0D) List of Functions	M ← N	[Input | Output] * (# of Functions)
(0x10) Read Variable	M → N	[Var ID]
(0x11) Variable's Value	M ← N	[Value]
(0x12) Read Group of Variables	M → N	[Group ID]
(0x13) Group of Variables' Values	M ← N	[Value] * (# of Vars in the Group)
(0x20) Write Variable	M → N	[Var ID, Value]
(0x22) Write Group of Variables	M → N	[Group ID], [Value]*(# of Vars in the Group)
(0x24) Binary Operation in a Variable	M → N	[Var ID, Operation,Mask]
(0x26) Binary Operation in a Group	M → N	[Group ID, Operation],[Mask]*(# of Vars in the Group)
(0x28) Write and Read Variables	M → N	[Var ID (to be written), Var ID (to be read), Value]
(0x30) Create Group of Variables	M → N	[Var ID] * (# of desired Vars)
(0x32) Remove all Groups of Variables	M → N
(0x40) Request Curve Block	M → N	[Curve ID, block offset (2 bytes)]
(0x41) Curve Block	M ↔ N	[Curve ID, block offset (2 bytes), Data (up to Sblock bytes)]*
(0x42) Recalculate Curve Checksum	M → N	[Curve ID]
(0x50) Execute Function	M → N	[Function ID, Input (between 0 and 15 bytes)]
(0x51) Function Return	M ← N	[Output (between 0 and 15 bytes)]
(0x53) Function Error	M ← N	[Error code]
Errors: (0xE0) OK, (0xE1) Malformed Message, (0xE2) Operation not supported, (0xE3) Invalid ID, (0xE4) Invalid Value, (0xE5) Invalid Payload Size, (0xE6) Read-Only, (0xE7) Insufficient Memory, (0xE8) Resource Busy

Table 10- Summary of the commands of the protocol

## (0x0_) Query commands
### (0x00) Query Protocol Version

Direction	Payload Size	Expected Answer
Master → Node	0	(0x01) Protocol Version
Description
Request the Version of the protocol supported by the Node.

### (0x01) Protocol Version

Direction	Payload Size		Expected Answer
Master ← Node	3		-
Description
The first byte is the Version field. The second one, the Subversion field. The third one, the Revision. A version string can be constructed with the format “Version.Subversion.Revision”. / Implementations of the same Version of the Protocol must be compatible. Greater Protocol's Subversion numbers mean that new commands were added. The Revision field is used to identify different implementations.
Structure
Payload / Version Subversion Revision
Example
Header Payload / 01 00 03 02 0A 00		Answer with Version 2, Subversion 10 and Revision 0: “2.10.0”.

### (0x02) Query List of Variables

Direction	Payload Size	Expected Answer
Master → Node	0	(0x03) List of Variables
Description
Request the list of Variables in the node.

### (0x03) List of Variables

Direction	Payload Size		Expected Answer
Master ← Node	(number of Variables in the node)		-
Description
Contains a list with the TYPE and the SIZE of all node's Variables.
Structure
Payload / First Variable ... Last Variable / TYPE (1 bit) | SIZE (7 bits) TYPE (1 bit) | SIZE (7 bits) / For each Variable is returned one byte of information. The Variables are in ascending order of their IDs. The first Variable has the ID 0. The most significant bit of each byte indicates if the Variable is read-only (bit = 0) or writable (bit = 1). The remaining seven bits contain the SIZE of the Variable. If SIZE is 0, the Variable is 128 bytes wide.
Example
Header Payload / 03 00 06 03 03 83 83 01 81		Two read-only Variables of size 3, two writable Variables of size 3, one read-only Variable of size 1, one writable Variable of size 1.

### (0x04) Query List of Group of Variables

Direction	Payload Size	Expected Answer
Master → Node	0	(0x05) List of Group of Variables
Description
Request the node to return a list describing all of his Groups of Variables.

### (0x05) List of Group of Variables

Direction	Payload Size		Expected Answer
Master ← Node	(number of Groups in the node)		-
Description
Contains a list with the TYPE and the SIZE of all node's Groups.
Structure
Payload / First Group ... Last Group / TYPE (1 bit) | SIZE (7 bits) TYPE (1 bit) | SIZE (7 bits) / One byte of information is returned for each Group in the node. The Groups are in their ascending ID order. The first Group has the ID 0. The most significant bit of each byte indicates the TYPE of the Group (0 for read-only, 1 for writable). The seven remaining bits contain the SIZE of the Group. If SIZE is 0, the Group has 128 Variables.
Example
Header Payload / 05 00 03 0A 05 85		Three Groups. The first one is read-only and has 10 Variables. The second one is also read-only and has 5 Variables. The last one is writable and has 5 Variables.

### (0x06) Query Group of Variables

Direction	Payload Size			Expected Answer
Master → Node	1			(0x07) Group of Variables
Description
Request the node to return the list of Variables of the specified Group.
Structure
Payload / Group ID			The Payload must contain the ID of the Group to be queried.
Example
Header Payload / 06 00 01 02			Query the Group with ID 2.
Possible Errors
(0xE3) Invalid ID:		There is no Group with the specified ID.

### (0x07) Group of Variables

Direction	Payload Size		Expected Answer
Master ← Node	(number of Variables in the Group)		-
Description
Contains the list of all Variables in the Group.
Structure
Payload / First Variable … Last Variable / ID ID		The Variable's IDs are listed in their ascending order.
Example
Header Payload / 07 00 05 04 05 06 07 09		Group of 5 Variables with IDs 4, 5, 6, 7 e 9.

### (0x08) Query List of Curves

Direction	Payload Size	Expected Answer
Master → Node	0	(0x09) List of Curves
Description
Request the list of Curves in the node.

### (0x09) List of Curves

Direction	Payload Size		Expected Answer
Master ← Node	5*(number of Curves in the node)		-
Description
Contains a list with TYPE, SBLOCK and NBLOCKS fields of all node's Curves.
Structure
Payload / First Curve ... Last Curve / TYPE SBLOCK NBLOCKS TYPE SBLOCK NBLOCKS / most sig. least sig. most sig. least sig. most sig. least sig. most sig. least sig. / The Curves are listed in the ascending order of their IDs. The first Curve has the ID 0. There are five bytes for each Curve. The first byte is the TYPE of the Curve (0 for read-only, 1 for writable). Second and third bytes contain the size of a block (SBLOCK). Fourth and fifth bytes contain the number of blocks (NBLOCKS). If NBLOCKS is 0, the Curve has 65536 blocks.
Example
Header Payload / 09 00 03 00 40 00 02 00		List with only one Curve. It is read-only (00) and has 512 (200h) 16384-byte (4000h) blocks.

### (0x0A) Query Curve Checksum

Direction	Payload Size			Expected Answer
Master → Node	1			(0x0B) Curve Checksum
Description
Request the CHECKSUM of a Curve in the node.
Structure
Payload / Curve ID			The ID of the Curve to be queried is specified.
Example
Header Payload / 0A 00 01 02			Query the CHECKSUM of the Curve with ID 2.
Possible Errors
(0xE3) Invalid ID:		There's no Curve with the ID specified.

### (0x0B) Curve Checksum

Direction	Payload Size	Expected Answer
Master ← Node	16	-
Description
Contains the CHECKSUM of a Curve.
Structure
Payload / MD5 Checksum / most significant least significant / The 16 bytes of the MD5 CHECKSUM are returned from the most to the least significant byte.
Example
Header Payload / 0B 00 10 01 23 45 67 89 AB CD EF FE DC BA 98 76 54 32 10 / Curve with CHECKSUM 0123456789abcdeffedcba9876543210.

### (0x0C) Query List of Functions

Direction	Payload Size	Expected Answer
Master ← Node	0	(0x0D) List of Functions
Description
Request the list of Functions in the node.

### (0x0D) List of Functions

Direction	Payload Size		Expected answer
Master ← Node	3*(number of Functions in the node)		-
Description
Contains a list with the INPUT and the OUTPUT of all node's Functions.
Structure
Payload / First Function ... Last Function / INPUT (4 bits) | OUTPUT (4 bits) INPUT (4 bits) | OUTPUT (4 bits) / The list of Functions are listed in the ascending order of their IDs. The first Function has the ID 0. There is one byte for each Function. The most significant nibble of the byte contains the INPUT length of the Function (between 0 and 15). Likewise, the least significant nibble contains the OUTPUT length of the Function (also between 0 and 15).
Example
Header Payload / 0D 00 03 F0 0F 22		Three Functions. The Function with ID 0 takes 15 bytes as input and returns 0 bytes as output. The Function with ID 1 returns 15 bytes as output and takes no input. The Function with ID 2 takes 2 bytes as input and returns 2 bytes as output.

## (0x1_) Reading Commands
### (0x10) Read Variable

Direction	Payload Size			Expected answer
Master → Node	1			(0x11) Variable's Value
Description
Request the VALUE of a Variable.
Structure
Payload / Variable ID			The payload contains the ID of the Variable to be read.
Example
Header Payload / 10 00 01 03			Request to read the Variable with ID 3.
Possible Errors
(0xE3) Invalid ID:		There's no Variable with the ID specified.
(0xE8) Resource Busy:		The Variable was in use and couldn't be read.

### (0x11) Variable's Value

Direction	Payload Size		Expected answer
Master ← Node	(SIZE of the Variable)		-
Description
Contains the VALUE of the Variable. The meaning of the VALUE of a Variable must be specified by the developer of the device.
Structure
Payload / Variable's VALUE / First byte … Last byte / The VALUE of the Variable is given byte by byte.
Example
Header Payload / 11 00 03 03 FF FF		Variable with the VALUE 03h FFh FFh.

### (0x12) Read Group of Variables

Direction	Payload Size			Expected answer
Master → Node	1			(0x13) Group of Variables' Values
Description
Request the VALUE of all Variables in a Group.
Structure
Payload / Group ID		The payload contains the ID of the Group to be read.
Example
Header Payload / 12 00 01 01		Request the VALUEs of the Variables in the Group with ID 1.
Possible Errors
(0xE3) Invalid ID:			There's no Group with the specified ID.
(0xE8) Resource Busy:			At least one Variable was in use and couldn't be read.

### (0x13) Group of Variables' Values

Direction	Payload Size	Expected answer
Master ← Node	(sum of SIZES of the Variables of a Group)	-
Description
Contains the VALUEs of all the Variables in a Group.
Structure
Payload / VALUE of the First Variable ... VALUE of the Last Variable / First byte … Last byte First byte … Last byte / The VALUEs of the Variables of the Group are listed in the ascending order of the Variables' IDs.
Example
Header Payload / 13 00 0C 03 FF FF 03 FF FF 03 FF FF 03 FF FF AA / Sequence of the VALUES of the Variables of a Group. It's possible to interpret those VALUES once it's known which Variables are in the Group (with (0x06) Query Group of Variables).

## (0x2_) Writing Commands
### (0x20) Write Variable

Direction	Payload Size			Expected answer
Master → Node	1 + (SIZE of the Variable)			(0xE0) OK
Description
Writes in the VALUE of a Variable. The Variable must be writable.
Structure
Payload / Variable ID Variable's VALUE / First byte … Last byte / The payload contains the ID of the Variable followed by the sequence of bytes to be written in the Variable's VALUE.
Example
Header Payload / 20 00 04 04 01 BB BB			Request to write 01h BBh BBh in the VALUE of the Variable with ID 4.
Possible Errors
(0xE3) Invalid ID:		There's no Variable with the specified ID.
(0xE6) Read-Only:		Variable can't be written (its TYPE is read-only).
(0xE8) Resource Busy:		The Variable was in use and couldn't be written.

### (0x22) Write Group of Variables

Direction	Payload Size		Expected answer
Master → Node	1+(sum of the SIZEs of the Variable's of a Group)		(0xE0) OK
Description
Contains values to be written to Variables in a specific Group. The Group must be writable.
Structure
Payload / Group ID VALUE of the first Variable ... VALUE of the last Variable / First byte … Last byte First byte … Last byte / The payload contains the ID of the Group followed by the bytes to be written in the VALUE field of all Group's Variables.
Example
Header Payload / 22 00 0E 02 01 BB BB 01 BB BB 01 BB BB 01 BB BB CC / Sequence of VALUES to be written in the Variables of the Group with ID 2. It's possible to interpret this particular sequence of values knowing the Variables of the Group (with the command (0x06) Query Group of Variables).
Possible Errors
(0xE3) Invalid ID:		There's no Group with the specified ID.
(0xE6) Read-Only:		Group couldn't be written (it's TYPE is read-only).
(0xE8) Resource Busy:		At least one Variable was in use and couldn't be written.

### (0x24) Binary Operation in a Variable

Direction	Payload Size			Expected answer
Master → Node	2+(SIZE of the Variable)			(0xE0) OK
Description
Perform a binary operation in the VALUE of a Variable with a specified mask. The available operations are listed in Table 11. The Variable must be writable. / Code Operation Description / 0x53 ('S') SET 'Turn on' (make 1) the bits specified in the mask. / 0x43 ('C') CLEAR 'Turn off' (make 0) the bits specified in the mask. / 0x54 ('T') TOGGLE Invert the bits specified in the mask. / 0x41 ('A') AND Perform a logical AND between the Variable's VALUE and the mask. / 0x4F ('O') OR Perform a logical OR between the Variable's VALUE and the mask. / 0x58 ('X') XOR Perform a logical XOR between the Variable's VALUE and the mask. / Table 11- Binary operations
Structure
Payload / Variable ID Operation Code Mask / First byte … Last byte / The payload contains the ID of the Variable and the code of the operation to be performed, followed by the bytes of the mask.
Example
Header Payload / 24 00 03 09 53 F0		Perform a SET operation (53h) in the Variable with ID 09h with the mask F0h, which will cause the most significant nibble of the Variable's VALUE to have all 1's.
Possible Errors
(0xE2) Operation not supported:			The binary operation requested isn't valid.
(0xE3) Invalid ID:			There's no Variable with the specified ID.
(0xE6) Read-Only:			Variable couldn't be written (its TYPE is read-only).
(0xE8) Resource Busy:			The Variable was in use and couldn't be written.

### (0x26) Binary Operation in a Group

Direction	Payload Size			Expected answer
Master → Node	1+(sum of the SIZEs of the Variable's of a Group)			(0xE0) OK
Description
Perform a binary operation in the VALUEs of the Variables of a Group with a specified mask. The available operations are listed in Table 11. The Group must be writable.
Structure
Payload / Group ID Operation Code First Mask ... Last Mask / First byte … Last byte First byte … Last byte / The payload contains the ID of the Group and the code of the operation to be performed, followed by the bytes of the masks.
Example
Header Payload / 26 00 05 02 4F 55 55 55		Perform an OR operation (4Fh) with the mask 55h in all bytes of all Variables' VALUEs in the Group with ID 02h.
Possible Errors
(0xE2) Operation not supported:			The requested binary operation is invalid.
(0xE3) Invalid ID:			There's no Group with the specified ID.
(0xE6) Read-Only:			Group couldn't be written (its TYPE is read-only).
(0xE8) Resource Busy:			At least one Variable was in use and couldn't be written.

### (0x28) Write and Read Variables

Direction	Payload Size			Expected answer
Master → Node	2 + (SIZE of the Variable to be written)			(0xE0) OK
Description
Writes in the VALUE of a Variable. The Variable must be writable. Returns the VALUE of a second Variable, to be read.
Structure
Payload / ID of the Variable to be written ID of the Variable to be read VALUE of the Variable to be written / First byte … Last byte / The payload contains the ID of the Variable to be written, followed by the ID of the Variable to be read and by sequence of bytes to be written.
Example
Header Payload / 20 00 05 04 05 01 BB BB			Request to write 01h BBh BBh to the VALUE of the Variable with ID 4. Request the VALUE of the Variable with ID 5.
Possible Errors
(0xE3) Invalid ID:		There's no Variable with the specified ID.
(0xE6) Read-Only:		Variable can't be written (its TYPE is read-only).
(0xE8) Resource Busy:		At least one Variable was in use and couldn't be written or read.

## (0x30) Group of Variables' Manipulation Commands
### (0x30) Create Group of Variables

Direction	Payload Size			Expected answer
Master → Node	(number of Variables in the Group)			(0xE0) OK
Description
Create a new Group of Variables with the Variables specified in the payload. The ID of the newly created Group is equal to the ID of the last Group in the node, plus 1.
Structure
Payload / First Variable … Last Variable / ID ID			The IDs of the Variables to be added to the new Group.
Example
Header Payload / 30 00 04 04 05 06 07		Create a Group with the Variables with IDs 4, 5, 6 and 7.
Possible Errors
(0xE3) Invalid ID:		At least one of the specified ID's doesn't exist.
(0xE5) Invalid Payload Size:		Number of Variables is zero or greater than the number of Variables in the node.
(0xE7) Insufficient Memory:		There's no memory available to create the Group.

### (0x32) Remove all Groups of Variables

Direction	Payload Size	Expected answer
Master → Node	0	(0xE0) OK
Description
Request for the node to remove all his Groups, except for the Standard Groups.

## (0x4_) Curve Transfer Commands
### (0x40) Request Curve Block

Direction	Payload Size			Expected answer
Master → Node	3			(0x41) Curve Block
Description
Request for the node to send a specific block of the specified Curve.
Structure
Payload / Curve ID Block offset / Most significant byte Least significant byte / The payload contains the ID of the Curve and two bytes for the block offset (in Big Endian). The first block has the offset zero (0000h).
Example
Header Payload / 40 00 03 03 00 04			Request the fifth block (0004h) of the Curve with ID 03h.
Possible Errors
(0xE3) Invalid ID:		There's no Curve with the specified ID.
(0xE4) Invalid Value:		The block offset specified is invalid.
(0xE8) Resource Busy:		The Curve was in use and couldn't be read.

### (0x41) Curve Block

Direction	Payload Size			Expected answer
Master ↔ Node	3 + (from 0 to SBLOCK)			(0xE0) OK
Description
Transmission of a Curve block sent either byte the node or by the master. If the block is sent by the master, it means that it is a request to write in the values of the specified block; the CHECKSUM of the Curve must be zeroed if the write operation is successful. When the master is done writing blocks to a Curve of the node, it should then send the (0x42) Recalculate Curve Checksum command. The block data can have less than SBLOCK bytes.
Structure
Payload / Curve ID Block Offset Block Data / Most significant byte Least significant byte First byte ... Last byte / The payload contains the ID of a Curve and two bytes for the offset of the Curve's block, followed by 16384 bytes containing the data of the specified block.
Example
Header Payload / 41 40 03 07 04 00 DD ... DD			Block offset 1024 (0400h) of the Curve with ID 07h that contains 16384 bytes DDh.
Possible Errors
(0xE3) Invalid ID:		There's no Curve with the specified ID.
(0xE4) Invalid Value:		The block offset specified is invalid.
(0xE6) Read-Only:		Curve couldn't be written (its TYPE is read-only).
(0xE8) Resource Busy:		The Curve was in use and couldn't be written.

### (0x42) Recalculate Curve Checksum

Direction	Payload Size			Expected answer
Master → Node	1			(0x0B) Curve Checksum
Description
Request that the CHECKSUM of a Curve be recalculated.
Structure
Payload / Curve ID			The payload contains the ID of the Curve to have its CHECKSUM recalculated.
Example
Header Payload / 42 00 01 00			Request to recalculate the CHECKSUM of the Curve with ID 0.
Possible Errors
(0xE3) Invalid ID:		There's no Curve with the specified ID.
(0xE8) Resource Busy:		The Curve was in use and couldn't be accessed.

## (0x5_) Function Execution Commands
### (0x50) Execute Function

Direction	Payload Size		Expected answers
Master → Node	1+(Function INPUT)		(0x51) Function Return or (0x53) Function Error
Description
Request a specific Function to be executed with the given parameters.
Structure
Payload / Function ID Input parameters / First byte ... Last Byte / The payload contains the ID of the Function to be executed followed by a list of bytes to be passed as input parameters. The amount of bytes for the input parameters must be exactly INPUT bytes.
Example
Header Payload / 50 00 03 01 BE 57		Execute the Function with ID 01h passing BEh 57h as input parameters.
Possible Errors
(0xE3) Invalid ID:		There's no Function with the specified ID.
(0xE5) Invalid Payload Size:		The number of bytes passed as input differs from the expected.

### (0x51) Function Return

Direction	Payload Size		Expected answer
Master ← Node	(Function OUTPUT)		-
Description
Contains the result of the execution of a Function.
Structure
Payload / Function output / First byte ... Last byte		The payload contains all bytes returned by the Function as output.
Example
Header Payload / 51 00 01 00		Response for the execution of a Function that returned just 1 byte, 00h.

### (0x53) Function Error

Direction	Payload Size		Expected answer
Master ← Node	1		-
Description
Indicates that there was an error returned by the execution of a Function.
Structure
Payload / Error Code		The payload contains the error code returned by the Function, which is specific to the Function and must have its meaning described by the developer of the device.
Example
Header Payload / 53 00 01 BB		An error return code of BBh.

## (0xE_) Error Commands
All Error Commands are in the direction Master ← Node and don't have payload.
### (0xE0) OK
Direction	Payload Size	Expected answer
Master ← Node	0	-
Description
The last command was successfully executed.

### (0xE1) Malformed Message
Direction	Payload Size	Expected answer
Master ← Node	0	-
Description
The number of bytes received in the payload differs from what was specified in the message's SIZE field.

### (0xE2) Operation not supported
Direction	Payload Size	Expected answer
Master ← Node	0	-
Description
The requested command is not supported.

### (0xE3) Invalid ID
Direction	Payload Size	Expected answer
Master ← Node	0	-
Description
One of the IDs specified was invalid.

### (0xE4) Invalid Value
Direction	Payload Size	Expected answer
Master ← Node	0	-
Description
A value passed is out of the acceptable range.

### (0xE5) Invalid Payload Size
Direction	Payload Size	Expected answer
Master ← Node	0	-
Description
The payload size is different than the size expected by the command.

### (0xE6) Read-Only
Direction	Payload Size	Expected answer
Master ← Node	0	-
Description
Tried to write on a read-only Entity.

### (0xE7) Insufficient Memory
Direction	Payload Size	Expected answer
Master ← Node	0	-
Description
There wasn't enough memory to complete the request.

### (0xE8) Resource Busy
Direction	Payload Size	Expected answer
Master ← Node	0	-
Description
The required resource was in use and, therefore, inaccessible.